## Functional Requirements
Procurement 26/00331: System for multi-gas analysis of off-gases, Ellinge Wastewater Treatment Plant (WWTP)
Annex Functional Requirements and Tender Prices
The Contract pertains to a system for multi-gas analysis of off-gases from nine wastewater treatment basins at the Ellinge wastewater treatment plant.
INSTRUCTIONS All “mandatory requirements” shall be met for all instruments tendered and shall preferably be answered with “YES” as affirmation of this. “Added value” items are ‘nice-to-have’ options described by VA SYD and are thus non-mandatory. Added value requirements result in a fictitious discount applied to the tender price in accordance with section 5.3 Added value in the tender documents. All fields marked orange are to be completed by the Tenderer. Note that operating costs and tender prices are itemised on a separate sheet.
Item | Requirements | Requirement type | Is the requirement met? | Enter values/reports/responses if relevant
1 | GENERAL PROVISIONS
1.1 | The Supplier shall comply with the legislation applicable to performance of the contract in Sweden. | Mandatory
1.2 | All equipment tendered shall be newly manufactured. | Mandatory
1.3 | All equipment tendered shall be CE marked in the prescribed manner, in accordance with applicable EU directives. | Mandatory
1.4 | All equipment tendered shall have a warranty period of at least two (2) years. | Mandatory
1.5 | The Supplier shall offer VA SYD the opportunity to purchase consumables and spare parts that are carried as standard by the Tenderer while the instrument is in operation. | Mandatory
1.6 | The Supplier shall guarantee access to spare parts, associated consumables, service, and software updates for at least three (3) years after the instrument tendered has been discontinued. | Mandatory
1.7 | All user interfaces shall be in Swedish or English. | Mandatory
2 | THE SYSTEM
2.1 | The system shall also be capable of measuring the volume concentration of nitrous oxide (N2O), methane (CH4), carbon dioxide (CO2), and oxygen (O2) in off-gas from at least one (1) wastewater treatment tank at a time. | Mandatory
2.2 | The off-gas shall be collected using floating hoods. | Mandatory
2.3 | The system shall be capable of measuring the off-gas from nine (9) different basins. | Mandatory
2.4 | It is simple to reduce the number of basins from which off-gas is collected and only measure the collected airflows, at no extra cost during implementation. | Added value
2.5 | Measurements shall be taken at least once (1) per hour from each basin, but preferably more frequently. | Mandatory
2.6 | Pre-treatment with particle filters shall be included as pre-treatment of off-gas before it is fed into the concentration measurement. | Mandatory
2.7 | The temperature of the off-gas being analysed shall be measured. | Mandatory
2.8 | The system shall be suitable for outdoor installation and have a minimum IP67 rating. | Mandatory
2.9 | The system shall be able to withstand ambient temperatures of between -20 °C and 40 °C. | Mandatory
2.10 | The system shall be able to withstand power failures without being damaged. | Mandatory
2.11 | The expected service life shall be at least ten (10) years. | Mandatory
2.12 | The Supplier shall provide written operating instructions, a functional description, and a drawing of the system in Swedish or English. | Mandatory
3 | CONCENTRATION METER
3.1 | The measuring range for nitrous oxide shall be 0–1000 ppmv. | Mandatory
3.2 | The measuring range for methane shall be 0–1000 ppmv. | Mandatory
3.3 | The measuring range for carbon dioxide shall be 0.04–4 vol.%. | Mandatory
3.4 | The measuring range for oxygen shall be 0–25% by volume. | Mandatory
3.5 | Automatic or controlled compensation for interference from other gases and other factors affecting the measurement of the respective gas shall be included. | Mandatory
3.6 | Automatic calibration of the meters shall be included, but this can be supported by manual calibration. | Mandatory
3.7 | If supplementary manual calibration is required, it shall be performed a maximum of (4) four times per year. | Mandatory
4 | HOODS
4.1 | Each hood shall collect off-gas from at least 0.8 m2 of basin surface area. | Mandatory
4.2 | The design and function of the hood and other gas collection components in the system shall be such that the system can handle any foam and condensate that enters or forms in the system. | Mandatory
5 | PLACEMENT
5.1 | The placement of floating hoods atop the basins and the available space for the remaining components alongside the basins are shown in Figure 1. | Mandatory
5.2 | Overview of one of the basin lines in Figure 2. | Mandatory
5.3 | The design of the aerator systems in the round basin and in one of the basin lines is shown in Figure 3 and Figure 4, respectively. | Mandatory
6 | DATA COMMUNICATION
6.1 | The Supplier shall be able to monitor the system’s performance, operation, and measurement data online via a cloud solution directly from the system. | Mandatory
6.2 | Data needed to determine the concentration of nitrous oxide, methane, carbon dioxide, and oxygen in the emissions from each hood shall be transmissible directly to VA SYD to Profibus or Profinet or via a protocol converter to Profibus or Profinet. | Mandatory
6.3 | Concentration data from each hood shall be directly transmissible from the system to VA SYD. | Mandatory
7 | OPERATION AND MAINTENANCE
7.1 | VA SYD personnel shall as a maximum be required to devote two weeks’ working time per annum on operating and maintaining the system. | Mandatory
Tenderer:

## Tender Prices
Procurement 26/00331: System for multi-gas analysis of off-gases, Ellinge Wastewater Treatment Plant (WWTP)
Annex Functional Requirements and Tender Prices
INSTRUCTIONS Tender prices are quoted prices that will constitute agreed prices throughout the contract term. Operating costs are other additional costs specified for the purpose of evaluating the total cost of the system.
Item | Price item | Quantity (weighting in evaluation) | Tendered price/cost (SEK)
TENDER PRICES
1. | Purchases including installation | 1
2. | Annual cost of service agreement | 10
3. | Replacement of concentration meters in the system (including installation) | 1
4. | Annual cost of any software license, including any upgrades. | 10
OPERATING COSTS
5. | Annual cost of calibration gases | 10
6. | Cost of replacing wear parts for a five-year period | 2
OPTION
7. | Hourly rate for consulting assistance on analysis of measurement data. | 0
Tenderer:
Note on C9: Patrik Adersjö: The ceiling price for purchases including installation of the system is SEK 900,000. The Client will not accept tender prices exceeding this ceiling price.